PROJECT QUALITY GATEKEEPER PROTOCOL (PQGP) Standard Operating Procedure for Commercial & Multi-Story Building Construction

DOC REF: SOP-QAQC-02 ¦ APPLICABILITY: General Contracting & Project Delivery ¦ GOVERNANCE: Tier-1

1. Protocol Mandate & Governance Architecture

The 5-Stage Project Quality Gatekeeper Protocol (PQGP) provides a non-negotiable governance and quality verification mechanism tailored for high-complexity building construction (commercial, residential, institutional, and mixed-use). Construction projects face substantial latent risks across structural integrity, architectural fit-out, statutory compliance, MEP integration, and commercial liability.

This protocol operates on the principle of Hard Gating: No project stage may mobilize, procure substantial works, or execute physical site installations until the designated Gatekeeper Committee conducts a formal review and issues a verified Gate Certificate.

| PASSED (GO) Unrestricted release to subsequent phase; budget and procurement unblocked. | CONDITIONAL PASS Phase mobilized with minor Punch-List actions resolved in <=14 days. | HOLD / REWORK Substandard deliverables. Rectification and mandatory re-audit required. | TERMINATE / KILL Critical structural defect, non-compliance, or commercially unviable overrun. |
| --- | --- | --- | --- |

2. Five-Stage Quality Gate Matrix

| Gate | Phase Scope | Primary Gatekeepers | Mandatory Deliverables | Kill / Hold Triggers |
| --- | --- | --- | --- | --- |
| Gate 1 (G1) | Pre-Construction & Design Verification | Project Manager, Principal Architect, Structural Lead | 100% IFC Drawings, BIM Clash Resolution, Geotechnical Sign-Off, Full Building Permits. | Unresolved spatial clashes; Missing foundational permits. |
| Gate 2 (G2) | Substructure & Foundation Sign-Off | Structural Engineer, Geotech Consultant, QA/QC Lead | Pile Load Test Reports (Static/Dynamic), Excavation As-Builts, Waterproofing Spark/Flood Tests, Rebar & Pour Log. | Pile settlement failure; Water ingress; Honeycombing > tolerance. |
| Gate 3 (G3) | Superstructure & Building Envelope | Structural Engineer, Project Manager, MEP Coordinator | 28-day Concrete Core Strength, Post-Tensioning Elongation Logs, AAMA Field Water Test, Formwork Scan Reports. | Concrete strength failure; Envelope water leakage. |
| Gate 4 (G4) | MEP Rough-in & Fit-Out | MEP Project in-charge, QA/QC Manager | Hydrostatic Pressure Tests (1.5x working), Duct Leakage (SMACNA), Firestopping Certifications, Above-Ceiling Sign-Off. | Unsealed fire dampers/shafts; Hydrostatic drop; Defective acoustic ratings. |
| Gate 5 (G5) | Commissioning & Closeout | Operation Team, QAQC Team, Client PM | Full Building TAB Report, Integrated Life-Safety Matrix Tripping, Certificate of Occupancy (C of O), O&M Manuals. | Fire Alarm / Generator transfer failure; Failed AHJ inspection, Equipmennt Motors, Fire pumps, Domestic Pumps, STP |

3. Detailed Stage Protocols & Execution Criteria

Gate 1: Pre-Construction, Constructability & Design Baseline

BIM Coordination: Zero 'Hard Clashes' between structural load-bearing elements and gravity drainage/HVAC mains (Navisworks Clash Log certified).

  - BIM Coordination:

The process of combining 3D digital blueprints from the architect, structural engineer, and 	mechanical/plumbing trades into one master computer model to make sure everything fits together.

  - Zero 'Hard Clashes':

No two physical solid objects occupy the exact same space in the computer model (for example, a large pipe isn't drawn directly through the middle of a solid steel column).

  - Structural load-bearing elements:

The critical "bones" that hold the building up and keep it standing—such as concrete columns, load-bearing walls, structural slabs, and steel beams.

  - Gravity drainage / HVAC mains:

The largest and most rigid utilities in a building:

  - Gravity drainage: Waste and sewer pipes that must slant downward at a strict angle so wastewater flows naturally. Because they need a constant slope, you cannot easily bend them around obstacles on-site.

  - HVAC mains: The largest central air ducts and chilled water pipes that heat, cool, and ventilate the building.

Geotechnical Validation: Bearing capacity and soil stabilization confirmed against foundation structural design parameters.

Permit Approvals: Brangay Clearance, environmental clearance, and city municipal building permits fully acquired.

Quality Baseline: Project schedule, 3d Construction Methodologies, Material Submittal Schedule (MSS), and Site Safety/Excavation Shoring Plans.

Gate 2: Substructure, Groundworks & Foundation Release

Pile Integrity & Load Tests: Geo Technical Analysis recommended by third party (BIP Steadfast)

Sub-Slab Barrier: Continuous blindside waterproofing inspection with spark testing / flood testing verified prior to slab casting.

Raft Mass Concreting: Thermal monitoring log for mass concrete pours (maximum core-to-surface temperature differential <= 20°C).

- Moisture Management (Curing)

- Start Immediately: Begin curing as soon as the concrete surface is hard enough to resist damage from the method used (usually right after the bleed water evaporates and final finishing is complete).

- Wet Methods: Keep the surface constantly wet using continuous water misting/sprinkling, ponding (for flat slabs), or covering with wet burlap/hessian blankets covered by polyethylene plastic sheeting to prevent evaporation.

- Chemical Curing Compounds: Spray an approved liquid membrane-forming curing compound that seals moisture inside the slab if wet curing is impractical.

- Duration: Maintain moisture continuously for a minimum of 7 days (or at least 3 days for high-early-strength concrete; 14 days for slow-curing/mass pours).

- Physical & Load Protection

- Foot Traffic: Keep all foot traffic off the slab for at least 24 to 48 hours.

- Heavy Equipment & Vehicles: Prohibit construction vehicles, machinery, and concentrated material loads for at least 7 to 28 days (until verified by test cylinder breaks).

- Formwork Striking Times: Do not strip side forms, vertical supports, or reshores prematurely; adhere to structural engineering schedules based on field-cured compressive strength.

- Early Contraction Joint Cutting

- Saw-cut control/contraction joints early—typically within 6 to 18 hours after pouring 	in warm weather (or 12 to 24 hours in cool weather)—before internal shrinkage stresses 	create random diagonal cracking.

- Cut joints to a depth of 1/4 the slab thickness.

Summary Checklist

| Priority | Key Action | Minimum Timeframe |
| --- | --- | --- |
| Immediate | Apply water mist, wet burlap, or curing compound | Hour 0 – Day 7 |
| Early | Saw-cut control joints | 6 – 18 Hours |
| Access | Restrict all personnel foot traffic | 24 – 48 Hours |
| Loads | Keep heavy vehicles and construction materials off | 7 – 28 Days |

Deliverables: Concrete plant calibration certs, 7/28-day break logs, surveyor coordinate map, and ground resistance (<= 5 Ohms), Certificate from supplier.

Gate 3: Superstructure Framing & Building Envelope Integrity

Framing & Tolerances: Laser scanning for slab deflection and verticality of columns/cores within ACI 117 / BS 5606 tolerances.

Envelope Field Tests: AAMA 501.2 hose testing and ASTM E1105 field water penetration testing for unitized curtain wall assemblies.

Roof Waterproofing: 48-hour hydrostatic flood test or electronic vector mapping (EVM) for green roofs and podium slabs.

Structural Sign-Off: Concrete cylinder compressive logs (28-day), NDT steel weld testing, and facade anchor pull-out test reports.

Gate 4: MEP Rough-in, Life Safety & Architectural Fit-Out

Pressure & Containment: Hydrostatic pressure testing of chilled water, domestic water, and sprinkler piping held at 150 psi for 24h with zero loss.

Firestopping Certification: 100% visual and destructive audit of UL-listed firestop penetration seals across floor/wall fire separations.

First-Off Mockups: Approved benchmark mockups for drywall finishes, tiling, joinery, and sanitary fixtures establishing tolerance baselines.

Above-Ceiling Sign-Off: Formal multi-disciplinary sign-off (HVAC, Electrical, Plumbing, Fire Alarm) prior to closing drywall ceilings.

Gate 5: Integrated Commissioning, Handover & Practical Completion

Black Building Test: Total main utility power disconnection to prove emergency generator start, ATS transfer, and life-safety operation <= 10s.

HVAC TAB Balancing: Airflow balance report, chilled water flow balancing, thermal comfort audit, and IAQ verification.

Statutory Sign-Off: Civil Defense smoke extraction, stair pressurization, and emergency voice alarm communication (EVAC) sign-off.

Closeout Assets: Final Certificate of Occupancy (C of O), As-Built BIM LOD 500 / COBie data, and O&M warranty dossiers.

4. Non-Conformance (NCR) & Escalation Hierarchy

| Severity Class | Definition & Construction Examples | Resolution Window | Gating Impact |
| --- | --- | --- | --- |
| Category 1 (Critical) | Structural deficiency, fire-life-safety non-compliance, failed load test, foundation compromise. | Immediate Stop-Work; Plan in 48h | Immediate Hard Stop / Gate Denied |
| Category 2 (Major) | Waterproofing failure, MEP pressure loss, unapproved material substitution, out-of-tolerance facade. | 7 Business Days | No Gate Clearance until rectified |
| Category 3 (Minor) | Surface finish imperfections, paint blemishes, missing labels, minor alignment flaws. | 7 Business Days | Conditional Pass permitted (Snag list) |

5. Quality Gate Approval & Certification Workflow

A Gate Review Meeting is convened at least 15 working days prior to target phase completion. The Project Quality Manager presents the Gate Review Dossier containing all ITP inspection records, lab test reports, as-built redlines, and third-party certifications. Sign-off requires unanimous assent from the voting committee:

| Stakeholder Role | Mandate & Review Responsibility | Authority Type | Sign-Off / Date |
| --- | --- | --- | --- |
| Client Representative / PM | Commercial alignment, schedule viability, and operational acceptance. | Voting Chair | [ ] Approved ___/___/20__ |
| Principal Structural / MEP Consultant | Technical specification compliance, code adherence, and design intent. | Technical Sign-Off | [ ] Approved ___/___/20__ |
| QA/QC Manager | Subcontractor quality auditing, NCR closeout, and inspection dossier completeness. | Executing Sign-Off | [ ] Approved ___/___/20__ |
| Independent CxA / Auditor | Special inspections, non-destructive testing, and building commissioning validation. | Advisory & Audit | [ ] Approved ___/___/20__ |